## Example Sheet
Job Name
Company Name
Available Fault Current Calculation
[9 empty] | by:John Sokolik | Ver. 4.00 |  | Three Single conductors | [5 empty] | Three Single conductors |  |  |  |  | Select Conductor & Raceway
Utility Fault Current |  |  |  | 0 | amperes | kVA = | 300 |  |  |  |  | in PVC raceway | [5 empty] | in Metal raceway |  |  |  |  | Copper in Nonmetallic Raceway
[6 empty] | E = | 0 |  |  |  |  | AWG | Copper | Alum. |  |  |  | AWG | Copper | Alum. |  |  | Aluminum in Nonmetallic Raceway
I = kVA x 1000 = trans. FLA |  |  |  |  | trans. FLA = |  | 0 |  |  |  | FALSE | 14 | 389.0593 | 236.9565 | #VALUE! | 0 | FALSE | 14 | 389.0593 | 236.9565 | #VALUE! |  | Copper in Metal Raceway
0 | [10 empty] | FALSE | 12 | 617.1195 | 375.9027 | #VALUE! | 0 | FALSE | 12 | 617.1195 | 375.9027 | #VALUE! |  | Aluminum in Metal Raceway
[11 empty] | FALSE | 10 | 981.6666 | 598.6547 | #VALUE! | 0 | FALSE | 10 | 981.6666 | 598.6547 | #VALUE!
Isca = trans. FLA x 100 |  |  | = |  |  | PF = | 90% |  |  |  | FALSE | 8 | 1558.7822 | 951.7579 | #VALUE! | 0 | FALSE | 8 | 1558.7822 | 951.7579 | #VALUE!
transformer Z | [5 empty] | Z = | 3% | % |  |  | FALSE | 6 | 2430.2358 | 1481.6945 | 1481.6945 | 0 | FALSE | 6 | 2425.2871 | 1480.5708 | 1480.5708
Isca = ampere short-circuit current RMS symmetrical. |  |  |  |  | Isca = |  | 3000 | amperes |  |  | FALSE | 4 | 3823.6322 | 2349.8944 | #VALUE! | 0 | FALSE | 4 | 3806.2231 | 2345.8361 | #VALUE!
[11 empty] | FALSE | 3 | 4635.4908 | 2871.799 | #VALUE! | 0 | FALSE | 3 | 4633.1288 | 2876.2446 | #VALUE!
Point to Point Method | [10 empty] | FALSE | 2 | 6044.2041 | 3729.7608 | #VALUE! | 0 | FALSE | 2 | 5906.9311 | 3713.3946 | #VALUE!
|  |  |  | Length (distance) |  | L = | 150 |  |  |  | FALSE | 1 | 7493.0777 | 4678.2818 | #VALUE! | 0 | FALSE | 1 | 7292.9819 | 4645.1729 | #VALUE!
'f ' factor = | 2 x L x I |  |  | (ASC) |  | Isca = | 3000 |  |  |  | FALSE | 1/0 | 9317.1278 | 5838.1225 | #VALUE! | 0 | FALSE | 1/0 | 8924.6983 | 5777.0769 | #VALUE!
| N x C x E L-N |  |  | # conductors per phase |  | N = | 1 |  |  |  | FALSE | 2/0 | 11423.7381 | 7301.3535 | #VALUE! | 0 | FALSE | 2/0 | 10755.1382 | 7186.6587 | #VALUE!
|  |  | Phase conductor constant |  |  | C = | 0 | Phase Conductor |  |  | FALSE | 3/0 | 13923.1885 | 9110.1284 | #VALUE! | 0 | FALSE | 3/0 | 12843.5014 | 8826.4313 | #VALUE!
|  |  |  | Volt Line to Line |  | E L - L = | 0 | Volt |  |  | FALSE | 4/0 | 16673.2215 | 11174.4748 | #VALUE! | 0 | FALSE | 4/0 | 15082.3387 | 10740.9899 | #VALUE!
[6 empty] | f = | 0 |  |  |  | FALSE | 250 kcmil | 18593.5928 | 12862.4199 | #VALUE! | 0 | FALSE | 250 | 16483.3921 | 12122.4589 | #VALUE!
|  |  | Neutral conductor constant |  |  | C = | 0 | Neutral Conductor |  |  | FALSE | 300 kcmil | 20867.7791 | 14922.7139 | #VALUE! | 0 | FALSE | 300 | 18176.5913 | 13909.6589 | #VALUE!
Multiplier |  |  |  | Volt Line to Neutral |  | E L - N = | 0 | Volt |  |  | FALSE | 350 kcmil | 22736.5524 | 16812.7788 | #VALUE! | 0 | FALSE | 350 | 19703.6016 | 15484.088 | #VALUE!
[6 empty] | f = | 0 |  |  |  |  | 400 kcmil | 24296.9785 | 18505.8303 |  | 0 |  | 400 | 20565.7729 | 16670.7191
| M = 1 | [10 empty] | 500 kcmil | 26706.1974 | 21390.9249 |  |  |  | 500 | 22185.1683 | 18755.8841
| 1 + f |  |  | Line to Line |  | M = | 1 |  |  |  |  | 600 kcmil | 28033.0986 | 23451.3811 |  |  |  | 600 | 22965.4578 | 20093.2481
|  |  |  | Line to Neutral |  | M = | 1 |  |  |  |  | 750 kcmil | 28303.9777 | 23491.9196 |  |  |  | 750 | 24136.5707 | 21766.3038
Fault Current at Service Equipment | [11 empty] | 1000 kcmil | 31490.6357 | 28778.9149 |  |  |  | 1000 | 25278.007 | 23477.7364
Isca x M = fault current at terminals of main disconnect L- L = | [7 empty] | 3000 | amperes
Isca x M = fault current at terminals of main disconnect L- N = | [7 empty] | 0 | amperes |  |  |  | Neutral | [9 empty] | 1
[12 empty] | 1 | 0 | CU/PVC | 0 | 0 | 1 | 0 | Select Voltage & Phase |  |  | 1 | -1
[12 empty] | 0 | 1.5 | AL/PVC | 0 | 0 |  | 0 | Single Phase 240/120 |  |  | 0 | 0
[13 empty] | 1 | CU/MET | 0 | 0 |  | 0 | Single Phase 208/120 |  |  | 0 | 0
Fault Current from |  | Service disc. to panel "_____" | [10 empty] | 1 | AL/MET | 0 | 0 |  | 0 | Three Phase 208/120 |  |  | 0 | 0 | 1 | TRUE | 0
[13 empty] | 1.5 |  | 0 | 0 |  | 0 | Single Phase 480/277 |  |  | 0 | 0 |  |  | 0
Single Phase Feeder |  |  |  | Length (distance) |  | L = | [6 empty] | 1 |  |  |  |  | 0 | Three Phase 480/277 |  |  | 0 | 0 | 1 |  | 0
'f ' factor = | 2 x L x I |  |  | (ASC) |  | Isca = | 3000 | Phase | 0 | Neutral |  | 1 | Neutral | 0 | 0 | 0 | 1 | neut |  | 0 | 0 | 1 | -1 | 0
| N x C x E L-N |  |  | # conductors per phase |  | N = | [7 empty] | 5711.8691 | 3650.6768 | 0 |  | 2 x L x I |  | 5377.5691 | 3593.3294 |  |  | 0
|  |  | Phase conductor constant |  |  | C = | 0 | Phase Conductor |  |  |  | 12 | Phase | 11423.7381 | 7301.3535 | 0 |  | phase | TRUE | 10755.1382 | 7186.6587 |  |  | 0
|  |  |  | Volt Line to Line |  | E L - L = | 0 | Volt |  |  |  |  | TRUE |  |  | 0 |  |  | TRUE |  |  |  |  | 0
[6 empty] | f = | 0 | [8 empty] | 0 | 1 | 2 x L x I | Single Phase |  | Single Phase Feeder |  |  | 0
|  |  | Neutral conductor constant |  |  | C = | 0 | Neutral Conductor | [9 empty] | 2 | Three Phase
|  |  |  | Volt Line to Neutral |  | E L - N = | 0 | Volt |  |  |  | 1 |  | 0 | 0 | 0 |  |  |  | 0 | 0
Multiplier | [5 empty] | f = | 0 | [6 empty] | 0 | 0 | 0 |  |  |  | 0 | 0
0
| M = 1 |  |  | Line to Line |  | M = | 1 |  |  |  |  | 1 | FALSE | 0 | 0 | 0 |  |  | FALSE | 0 | 0
| 1 + f |  |  | Line to Neutral |  | M = | 1 | [8 empty] | 0
[12 empty] | 1 |  | CU/PVC | 0 | 0 |  |  | Single Phase Feeder
Isca x M = fault current at terminals of the panel L- L = | [7 empty] | 3000 | amperes |  |  |  |  | AL/PVC | 0 | 0
Isca x M = fault current at terminals of the panel L- N = | [7 empty] | 0 | amperes |  |  |  |  | CU/MET | 0 | 0
[14 empty] | AL/MET | 0 | 0
| Calculation does not include motor contribution | [13 empty] | 0 | 0
0
[16 empty] | 0 | [6 empty] | 0
[22 empty] | 0 | -1
[22 empty] | 0 | 0
Branch Circuit Fault from |  |  | Point to Point | [18 empty] | 0 | 0
[22 empty] | 0 | 0 | 1 | TRUE | 0
Single Phase Branch |  |  |  | Length (distance) |  | L = | [15 empty] | 0 | 0 |  |  | 0
'f ' factor = | 2 x L x I |  |  | (ASC) |  | Isca = | 3000 | Phase | 0 | Neutral | [11 empty] | 0 | 0 | 1 |  | 0
| N x C x E L-N |  |  | # conductors per phase |  | N = | [15 empty] | 0 | -1 | -1
|  |  | Phase conductor constant |  |  | C = | 0 | Phase Conductor | [7 empty] | u65 | 1 | [6 empty] | 1
|  |  |  | Volt Line to Line |  | E L - L = | 0 | Volt | [15 empty] | 0
[6 empty] | f = | 0 | [8 empty] | u67 | 1 | 2 x L x I | Single Phase |  | Single Phase Branch |  |  | 0
|  |  | Neutral conductor constant |  |  | C = | 0 | Neutral Conductor | [9 empty] | 2 | Three Phase |  |  |  |  | 0
|  |  |  | Volt Line to Neutral |  | E L - N = | 0 | Volt |  |  |  | 1 |  | 0 | 0 | 0 |  |  |  | 0 | 0
Multiplier | [5 empty] | f = | 0 | [6 empty] | 0 | 0 | 0 |  |  |  | 0 | 0
0
| M = 1 |  |  | Line to Line |  | M = | 1 |  |  |  |  | 1 | FALSE | 0 | 0 | 0 |  |  | FALSE | 0 | 0
| 1 + f |  |  | Line to Neutral |  | M = | 1 | [8 empty] | 0
[12 empty] | 1 |  | CU/PVC | 0 | 0 |  |  | Single Phase Branch
Isca x M = fault current at terminals of the panel L- L = | [7 empty] | 3000 | amperes |  |  |  |  | AL/PVC | 0 | 0
Isca x M = fault current at terminals of the panel L- N = | [7 empty] | 0 | amperes |  |  |  |  | CU/MET | 0 | 0 |  |  | 1 |  | 0
[14 empty] | AL/MET | 0 | 0 |  |  | 0
| Calculation does not include motor contribution | [13 empty] | 0 | 0 |  |  | -1 | 0 | -1
[19 empty] | 0 | 1 | 1
[19 empty] | -1 | 1 | 1 | 1
0
0
Note on F8: When the fault current is provided by the governing utility insert the value here. KVA and transformer impedence is not required to continue. Go to L= ,and insert footage of conductor length.
Note on I8: If you have inserted the Utility Fault Current amps, inserting the kVA in this cell is not required. If available fault current is not known, insert transformer kVA rating here.
Note on I9: This value will be filled in when you 'Select Voltage & Phase' from the first dropdown box
Note on I14: If you have inserted the Utility Fault Current amps inserting trans. impedence in this cell is not required. If transformer fault current is not known, insert transformer impedence here.
Note on I18: Enter the length of one phase conductor in the group
Note on I20: Enter the number of electrical conductors per phase between the transformer and the equipment
Note on I21: Select a conductor and raceway from the top drop down box Then select phase conductor size from AWG drop down box.
Note on I24: Select neutral conductor size from AWG drop down box.
Note on I40: Data from above calculation
Note on I42: To select a conductor check the appropriate box to the right of the largest phase conductor
Note on I63: Data from above calculation
Note on I65: To select a conductor check the appropriate box to the right of the largest phase conductor
Note on K40: Data from above calculation
Note on K63: Data from above calculation
Note on P35: Neutral , Choose formula ref point
Note on P49: Link cell to conductor size
Note on P72: Link cell to conductor size
Note on V34: =choose(U34,0,208,208,480,480) Link to cell I9 for select voltage
Note on V35: =choose(U34,0,240,208,208,480,480) Link to cell I9 for select voltage
Note on V36: =choose(U34,0,208,208,480,480) Link to cell I9 for select voltage
Note on V37: =CHOOSE(U34,0,I8*1000/I9,I8*1000/I9,I8*1000/I9*1.732,I8*1000/I9,I8*1000/I9*1.732) Link to cell I9 for select voltage
Note on V38: =choose(U34,0,120,120,120,277,277) Link to nuetral voltage
Note on V39: =choose(U34,0,240,208,208,480,480) Link to line to line voltage
Note on V41: =choose(U34,0,240,208,208,480,480) Link to cell I9 for select voltage
Note on V44: =choose(U34,0,240,208,208,480,480) Link to cell I9 for select voltage
Note on V49: Link cell to conductor size
Note on V67: =choose(U34,0,240,208,208,480,480) Link to cell I9 for select voltage
Note on V72: Link cell to conductor size
Note on W79: when cell = -1 then feeder is 3ph
Note on W80: when cell = -1 then feeder is 3ph
Note on X79: if cell = 1 then branch is 1ph
Note on X80: if cell = 1 then branch is 1ph
Step 1b: Insert the kVA rating (PF) power factor and (Z) impedence of transformer. (Note: When you insert the kVA rating, power factor and impedence you must select a voltage from the select the Voltage and Phase from dropdown box before the value will be calculated.)
or
Step 1a: Insert available
fault current ampere rating from local utility
Step 3: Insert the Length of one conductor
Step 4: Insert the number of conductors per phase.
Step 2: Select type of conductor and conduit
Step 5b: Select neutral conductor size.
Step 5a: Select phase
conductor size size.
Finished product
CALCULATED FAULT CURRENT
Personalize by entering
the 'Job Name' and
'Your Company Name'
Continue by entering next point to point

## Fault Current Calculation
Project Name
Your Company Name
Available Fault Current Calculation
[9 empty] | by:John Sokolik | Ver. 2014 |  | Three Single conductors | [5 empty] | Three Single conductors |  |  |  |  | Select Conductor & Raceway | [13 empty] | Yellow cells are fields for data input, Use the TAB button to move from field to field. See example sheet tab at the lower left corner of this sheet. Place cursor over this message for further information.
Utility Fault Current |  |  |  |  | amperes | kVA = |  |  | jmp1jds@comcast.net |  |  | in PVC raceway | [5 empty] | in Metal raceway |  |  |  |  | Copper in Nonmetallic Raceway
[6 empty] | E = | 0 |  |  |  |  | AWG | Copper | Alum. |  |  |  | AWG | Copper | Alum. |  |  | Aluminum in Nonmetallic Raceway
I = kVA x 1000 = trans. FLA |  |  |  |  | trans. FLA = |  | 0 |  |  |  | FALSE | 14 | 389.0593 | 236.9565 | #VALUE! | 0 | FALSE | 14 | 389.0593 | 236.9565 | #VALUE! |  | Copper in Metal Raceway
0 | [10 empty] | FALSE | 12 | 617.1195 | 375.9027 | #VALUE! | 0 | FALSE | 12 | 617.1195 | 375.9027 | #VALUE! |  | Aluminum in Metal Raceway
[11 empty] | FALSE | 10 | 981.6666 | 598.6547 | #VALUE! | 0 | FALSE | 10 | 981.6666 | 598.6547 | #VALUE!
Isca = trans. FLA x 100 x PF |  |  |  | = |  | PF = |  |  |  |  | FALSE | 8 | 1558.7822 | 951.7579 | #VALUE! | 0 | FALSE | 8 | 1558.7822 | 951.7579 | #VALUE!
transformer Z | [5 empty] | Z = |  |  |  |  | FALSE | 6 | 2430.2358 | 1481.6945 | 1481.6945 | 0 | FALSE | 6 | 2425.2871 | 1480.5708 | 1480.5708
Isca = ampere short-circuit current RMS symmetrical. |  |  |  |  | Isca = |  | 0 | amperes |  |  | FALSE | 4 | 3823.6322 | 2349.8944 | #VALUE! | 0 | FALSE | 4 | 3806.2231 | 2345.8361 | #VALUE!
[11 empty] | FALSE | 3 | 4635.4908 | 2871.799 | #VALUE! | 0 | FALSE | 3 | 4633.1288 | 2876.2446 | #VALUE! |  | 1 | 1 | FEET
Point to Point Method | [10 empty] | FALSE | 2 | 6044.2041 | 3729.7608 | #VALUE! | 0 | FALSE | 2 | 5906.9311 | 3713.3946 | #VALUE! |  |  | 3.281 | METERS
|  |  | Length (distance) |  |  | L = |  |  |  |  | FALSE | 1 | 7493.0777 | 4678.2818 | #VALUE! | 0 | FALSE | 1 | 7292.9819 | 4645.1729 | #VALUE!
'f ' factor = | 2 x L x I |  |  | (ASC) |  | Isca = | 0 |  |  |  | FALSE | 1/0 | 9317.1278 | 5838.1225 | #VALUE! | 0 | FALSE | 1/0 | 8924.6983 | 5777.0769 | #VALUE! |  |  | 1
| N x C x E L-N |  |  | # conductors per phase |  | N = |  |  |  |  | FALSE | 2/0 | 11423.7381 | 7301.3535 | #VALUE! | 0 | FALSE | 2/0 | 10755.1382 | 7186.6587 | #VALUE!
|  |  | Phase conductor constant |  |  | C = | 0 | Phase Conductor |  |  | FALSE | 3/0 | 13923.1885 | 9110.1284 | #VALUE! | 0 | FALSE | 3/0 | 12843.5014 | 8826.4313 | #VALUE!
|  |  |  | Volt Line to Line |  | E L - L = | 0 | Volt |  |  | FALSE | 4/0 | 16673.2215 | 11174.4748 | #VALUE! | 0 | FALSE | 4/0 | 15082.3387 | 10740.9899 | #VALUE!
[6 empty] | f = | 0 |  |  |  | FALSE | 250 kcmil | 18593.5928 | 12862.4199 | #VALUE! | 0 | FALSE | 250 | 16483.3921 | 12122.4589 | #VALUE!
|  |  | Neutral conductor constant |  |  | C = | 0 | Neutral Conductor |  |  | FALSE | 300 kcmil | 20867.7791 | 14922.7139 | #VALUE! | 0 | FALSE | 300 | 18176.5913 | 13909.6589 | #VALUE!
Multiplier |  |  |  | Volt Line to Neutral |  | E L - N = | 0 | Volt |  |  | FALSE | 350 kcmil | 22736.5524 | 16812.7788 | #VALUE! | 0 | FALSE | 350 | 19703.6016 | 15484.088 | #VALUE!
[6 empty] | f = | 0 |  |  |  |  | 400 kcmil | 24296.9785 | 18505.8303 |  | 0 |  | 400 | 20565.7729 | 16670.7191
| M = 1 | [10 empty] | 500 kcmil | 26706.1974 | 21390.9249 |  |  |  | 500 | 22185.1683 | 18755.8841
| 1 + f |  |  | Line to Line |  | M = | 1 |  |  |  |  | 600 kcmil | 28033.0986 | 23451.3811 |  |  |  | 600 | 22965.4578 | 20093.2481
|  |  |  | Line to Neutral |  | M = | 1 |  |  |  |  | 750 kcmil | 28303.9777 | 23491.9196 |  |  |  | 750 | 24136.5707 | 21766.3038
Fault Current at Service Equipment | [11 empty] | 1000 kcmil | 31490.6357 | 28778.9149 |  |  |  | 1000 | 25278.007 | 23477.7364
Isca x M = fault current at terminals of main disconnect L- L = | [7 empty] | 0 | amperes
Isca x M = fault current at terminals of main disconnect L- N = | [7 empty] | 0 | amperes |  |  |  | Neutral | [9 empty] | 1
[12 empty] | 1 | 0 | CU/PVC | 0 | 0 | 1 | 0 | Select Voltage & Phase
[12 empty] | 0 | 1.5 | AL/PVC | 0 | 0 |  | 0 | Single Phase 240/120
[12 empty] | 220/127V | 1.5 | CU/MET | 0 | 0 |  | 0 | Single Phase 220/127 (Mexico)
Fault Current from |  | Service Equipment to Panel __ | [10 empty] | 1 | AL/MET | 0 | 0 |  | 0 | Single Phase 208/120
[13 empty] | 1 | [5 empty] | Three Phase 208/120
Single Phase Feeder |  |  |  | Length (distance) |  | L = | [6 empty] | 1 | [5 empty] | Three Phase 220/127
'f ' factor = | 2 x L x I |  |  | (ASC) |  | Isca = | 0 | Phase | 0 | Neutral |  | 380/220V | 1 |  | 0 | 0 |  | 0 | Three Phase 380/220
| N x C x E L-N |  |  | # conductors per phase |  | N = | [6 empty] | 1 |  |  |  |  | 0 | Three Phase 416/240 | [5 empty] | S.E. | 0
|  |  | Phase conductor constant |  |  | C = | 0 | Phase Conductor |  |  |  |  | 1 | [5 empty] | Single Phase 480/277 | [5 empty] | BR | 1
|  |  |  | Volt Line to Line |  | E L - L = | 0 | Volt |  |  |  |  | 1 | [5 empty] | Three Phase 480/277
[6 empty] | f = | 0 | [5 empty] | 1 | [5 empty] | Three Phase 600/347 | [6 empty] | 1 | NEG = BAD
|  |  | Neutral conductor constant |  |  | C = | 0 | Neutral Conductor
|  |  |  | Volt Line to Neutral |  | E L - N = | 0 | Volt |  |  |  | 1 | Neutral | 0 | 0 | 0 | 1 | neut |  | 0 | 0 | [6 empty] | 1 |  | 0 | 0 | 0 |  | 0 | 0
Multiplier | [5 empty] | f = | 0 | [6 empty] | 0 | 0 | 0 |  | 2 x L x I |  | 0 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0
[12 empty] | 1 | Phase | 0 | 0 | 0 |  | phase | TRUE | 0 | 0 | [10 empty] | 0
| M = 1 |  |  | Line to Line |  | M = | 1 | [5 empty] | TRUE |  |  | 0 |  |  | TRUE | [8 empty] | 1 | FALSE | 0 | 0 | 0 | FALSE | 0 | 0
| 1 + f |  |  | Line to Neutral |  | M = | 1 | [8 empty] | 0 | 1 | 2 x L x I | Single Phase |  | Single Phase Feeder | [10 empty] | 0
[18 empty] | 2 | Three Phase | [8 empty] | 1 |  | CU/PVC | 0 | 0 | Single Phase Feeder |  |  | 1
Isca x M = fault current at terminal of the panel L- L = | [7 empty] | 0 | amperes | [20 empty] | AL/PVC | 0 | 0
Isca x M = fault current at terminal of the panel L- N = | [7 empty] | 0 | amperes | [20 empty] | CU/MET | 0 | 0
[30 empty] | AL/MET | 0 | 0
| Calculation does not include motor contribution | [29 empty] | 0 | 0
0
[16 empty] | 0 | [6 empty] | 0
[22 empty] | 0 | -1
[22 empty] | 0 | 0
Branch Circuit Fault from |  |  | (example) FROM PANEL TO OUTLET | [18 empty] | 0 | 0
[22 empty] | 0 | 0 | 1 | TRUE | 0
Single Phase Branch |  |  |  | Length (distance) |  | L = | [15 empty] | 0 | 0 |  |  | 0
'f ' factor = | 2 x L x I |  |  | (ASC) |  | Isca = | 0 | Phase | 0 | Neutral | [11 empty] | 0 | 0 | 1 |  | 0
| N x C x E L-N |  |  | # conductors per phase |  | N = | [15 empty] | 0 | -1 | -1
|  |  | Phase conductor constant |  |  | C = | 0 | Phase Conductor | [7 empty] | u65 | 1 | [6 empty] | 1
|  |  |  | Volt Line to Line |  | E L - L = | 0 | Volt | [15 empty] | 0
[6 empty] | f = | 0 | [5 empty] | DROP DOWN 1 OR 3 |  |  | u67 | 1 | 2 x L x I | Single Phase |  | Single Phase Branch |  |  | 0
|  |  | Neutral conductor constant |  |  | C = | 0 | Neutral Conductor | [9 empty] | 2 | Three Phase |  |  |  |  | 0
|  |  |  | Volt Line to Neutral |  | E L - N = | 0 | Volt |  |  |  | 1 |  | 0 | 0 | 0 |  |  |  | 0 | 0
Multiplier | [5 empty] | f = | 0 | [6 empty] | 0 | 0 | 0 |  |  |  | 0 | 0
0
| M = 1 |  |  | Line to Line |  | M = | 1 |  |  |  |  | 1 | FALSE | 0 | 0 | 0 |  |  | FALSE | 0 | 0
| 1 + f |  |  | Line to Neutral |  | M = | 1 | [8 empty] | 0
[12 empty] | 1 |  | CU/PVC | 0 | 0 |  |  | Single Phase Branch |  |  | 1
Isca x M = fault current at terminal of the panel L- L = | [7 empty] | 0 | amperes |  |  |  |  | AL/PVC | 0 | 0
Isca x M = fault current at terminal of the panel L- N = | [7 empty] | 0 | amperes |  |  |  |  | CU/MET | 0 | 0 |  |  | 1 |  | 0
[14 empty] | AL/MET | 0 | 0 |  |  | 0
| Calculation does not include motor contribution | [13 empty] | 0 | 0 |  |  | -1 | 0 | -1
[19 empty] | 0 | 1 | 1
[19 empty] | -1 | 1 | 1 | 1
0
0
Note on F8: When the fault current is provided by the governing utility insert the value here. The KVA, power factor (PF) and impedence (Z) of the transformer is not required to continue. Go to L= ,and insert footage of conductor length. Use 'Edit', 'Clear', Comments' to clear any input cell.
Note on I8: If you have inserted the Utility Fault Current amps, inserting the kVA in this cell is not required. If available fault current is not known, insert transformer kVA rating here.
Note on I13: Inserting a (PF) power factor is only required when using method 1b, see example sheet tab in lower left of the sheet. The (PF) default for this cell should be 100% unless the power factor is known.
Note on I14: If you have inserted the Utility Fault Current amps inserting trans. impedence in this cell is not required. If transformer fault current is not known, insert transformer impedence here.
Note on I18: Enter the length of one phase conductor in the group
Note on I20: Enter the number of electrical conductors per phase between the transformer and the service equipment
Note on I21: Select a Phase Cconductor and raceway from the top drop down box Then select phase conductor size from AWG drop down box.
Note on I24: Select neutral conductor size from AWG drop down box.
Note on I39: Enter the length of one phase conductor in the group
Note on I40: Data from above calculation
Note on I41: Enter the number of electrical conductors per phase between the service equipment and this panel or disconnect.
Note on I42: To select a phase conductor constant select the size conductor from the drop-down box to the right.
Note on I45: To select a neutral conductor constant select the size conductor from the drop-down box to the right.
Note on I62: Enter the length of one phase conductor in the group
Note on I63: Data from above calculation
Note on I65: To select a phase conductor constant select the size conductor from the drop-down box to the right.
Note on I68: To select a neutral conductor constant select the size conductor from the drop-down box to the right.
Note on K40: Data from above calculation
Note on K63: Data from above calculation
Note on P35: Neutral , Choose formula ref point
Note on P72: Link cell to conductor size
Note on V34: =choose(U34,0,208,208,480,480) Link to cell I9 for select voltage
Note on V35: =choose(U34,0,240,208,208,480,480) Link to cell I9 for select voltage
Note on V36: =choose(U34,0,208,208,480,480) Link to cell I9 for select voltage
Note on V37: =CHOOSE(U34,0,I8*1000/I9,I8*1000/I9,I8*1000/I9*1.732,I8*1000/I9,I8*1000/I9*1.732) Link to cell I9 for select voltage
Note on V40: =choose(U34,0,120,120,120,277,277) Link to nuetral voltage
Note on V41: =choose(U34,0,240,208,208,480,480) Link to line to line voltage
Note on V47: =choose(U34,0,240,208,208,480,480) Link to cell I9 for select voltage
Note on V50: =choose(U34,0,240,208,208,480,480) Link to cell I9 for select voltage
Note on V67: =choose(U34,0,240,208,208,480,480) Link to cell I9 for select voltage
Note on V72: Link cell to conductor size
Note on W79: when cell = -1 then feeder is 3ph
Note on W80: when cell = -1 then feeder is 3ph
Note on X79: if cell = 1 then branch is 1ph
Note on X80: if cell = 1 then branch is 1ph
Note on AC41: John DeLong: 1 SINGLE PHASE 3 THREE PHASE
Note on AD44: John DeLong: LINK BETWEEN 1 OR 3 PH SERVICE ENTRANCE DROP DOWN AND 1 OR 3 PH FEEDER DROP DOWN BOXES
Note on AF49: Link cell to conductor size
Note on AL49: Link cell to conductor size
Note on DN7: Any cell with a red corner has a comment to help guide you through this calculation. Just place your cursor over the yellow cell and the comment box will open. Not all yellow cells need to have data inserted, they are the first three input cells identified as step 1a or 1b in the example sheet.