Conductor Sizing and Overcurrent Protection Continued….

As a follow-up to Mike Holt's article on conductor sizing and overcurrent protection(http://www.mikeholt.com/Newsletters/conductorsize-protection.htm), this article will address an additional criteria for conductor sizing that is often overlooked, short-circuit protection of conductors.

Short-circuit protection of conductors depends upon the available fault current and the type and speed of the overcurrent protection device.  If one looks at the fine print note in Section 240-1, it alludes to the fact that other requirements are present for conductor protection as well and reads:

"FPN: Overcurrent Protection for conductors and equipment is provided to open the circuit if the current reaches a value that will cause an excessive or dangerous temperature in conductors or conductor insulation.  See also Section 110-9 for requirements for interrupting rating and Section 110-10 for requirements for protection against fault currents."

Section 110-9 addresses the interrupting rating of the overcurrent device required based upon short-circuit current.  Section 110-10 addresses the overcurrent protective device, component short-circuit current ratings and protection of the circuit components by the overcurrrent protective device to prevent "excessive damage".  This is especially important because it is not just protection against overloads, it is also protection from short-circuits.

Introduction:

Now the question remains, how can we verify protection of conductors from "extensive damage" against short-circuits? The answer depends upon the interpretation of "extensive damage". Information on conductor short-circuit current is available based upon the amount of damage the user allows.  One level of protection is based upon the insulation of the conductor.  Formulas and charts from the IEC and the Insulated Cable Engineers Association (ICEA) are available to illustrate this level of protection.  The charts determine how much time and current is required to raise the temperature of the conductor from the operating temperature to a temperature where slight damage to thermoplastic insulation occurs.  For conductors with 75 deg. C thermoplastic insulation, the damaging temperature is typically 150 deg. C.  Another level of protection is based on the Soares "validity" rating.  The validity rating corresponds to the amount of current required to cause the copper to become loose under a lug after the conductor has had a chance to cool back down.  This validity rating is based upon raising the copper temperature from 75 deg. C to 250 deg. C, which is the annealing temperature of copper.  In addition, a third level of protection promoted by Onderdonk allows the calculation of the current necessary to cause the conductor to melt (75 deg. C to 1,083 deg. C).

Table 1 illustrates the conductor rating for 5 seconds as well as the maximum I2t (ampere2 seconds) rating based upon conductor size and the conductor damage level (ICEA, Soares or Onderdonk).

However, depending upon the damage level selected, the overcurrent protective device selected and the resulting opening time, the amount of current the conductor can handle will need to be adjusted.  If we select the ICEA insulation damage level as the desired protection level for conductors, we can establish more usable information with respect to the clearing time of the overcurrent protective device.  Since some devices such as airframe/power circuit breakers exist which can have short-time delays up to 30 cycles, we must analyze the opening time up to this level.  Table 2 shows the amount of current the conductor can handle based upon different clearing times (up to 30 cycles) with respect to the ICEA insulation damage level.

| Table 1: Comparison of Conductor Current Ratings (Based on RMS Amperes) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 5 Second Rating (Amps) |  |  | I2t Rating (Amperes Squared Seconds) |  |  |  |
| Cond | Cond | ICEA | Soares | Onderdonk | ICEA | Soares | Onderdonk |  |
| Size | Area | Insulation | Annealing | Melting | Insulation | Annealing | Melting |  |
|  | Circ. Mils | 150 Deg. C | 250 Deg. C | 1083 Deg. C | 150 Deg. C | 250 Deg. C | 1083 Deg. C |  |
| 14 | 4110 | 97.31 | 139.84 | 251.35 | 47346 | 97774 | 315881 |  |
| 12 | 6530 | 154.61 | 222.18 | 399.34 | 119517 | 246812 | 797382 |  |
| 10 | 10380 | 245.76 | 353.17 | 634.79 | 301994 | 623640 | 2014813 |  |
| 8 | 16510 | 390.90 | 561.74 | 1009.68 | 764007 | 1577732 | 5097229 |  |
| 6 | 26240 | 621.27 | 892.79 | 1604.72 | 1929882 | 3985352 | 12875605 |  |
| 4 | 41740 | 988.25 | 1420.16 | 2552.63 | 4883238 | 10084258 | 32579535 |  |
| 3 | 52620 | 1245.85 | 1790.34 | 3218.00 | 7760768 | 16026576 | 51777572 |  |
| 2 | 66360 | 1571.17 | 2257.83 | 4058.27 | 12342860 | 25488942 | 82347942 |  |
| 1 | 83690 | 1981.48 | 2847.46 | 5118.10 | 19631350 | 40540229 | 130974616 |  |
| 1/0 | 105600 | 2500.23 | 3592.93 | 6458.01 | 31255818 | 64545637 | 208529659 |  |
| 2/0 | 133100 | 3151.33 | 4528.59 | 8139.79 | 49654561 | 102540438 | 331280679 |  |
| 3/0 | 167800 | 3972.91 | 5709.22 | 10261.88 | 78919977 | 162975743 | 526530956 |  |
| 4/0 | 211600 | 5009.94 | 7199.46 | 12940.49 | 125497294 | 259161440 | 837281168 |  |
| 250 | 250000 | 5919.11 | 8505.98 | 15288.86 | 175179408 | 361758775 | 1168745667 |  |
| 300 | 300000 | 7102.93 | 10207.18 | 18346.63 | 252258347 | 520932636 | 1682993761 |  |
| 350 | 350000 | 8286.76 | 11908.38 | 21404.40 | 343351639 | 709047199 | 2290741508 |  |
| 400 | 400000 | 9470.58 | 13609.57 | 24462.17 | 448459284 | 926102464 | 2991988908 |  |
| 500 | 500000 | 11838.22 | 17011.97 | 30577.71 | 700717631 | 1447035100 | 4674982669 |  |

| Table 2: Maximum Short-Circuit Current Rating In Amperes (Per ICEA Insulation Damage) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Maximum Short-Circuit Current Rating In RMS Amperes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cond | Cond | 1/2* | 1 | 2 | 3 | 6 | 12 | 18 | 24 |  | 30 |  |  |  |  |  |
| Size | Area | Cycles | Cycle | Cycle | Cycle | Cycle | Cycle | Cycle | Cycle |  | Cycle |  |  |  |  |  |
|  | Circ. Mils | 0.0083 | 0.0167 | 0.0333 | 0.0500 | 0.1 | 0.2 | 0.3 | 0.4 |  | 0.5 |  |  |  |  |  |
|  |  | Seconds | Seconds | Seconds | Seconds | Seconds | Seconds | Seconds | Seconds |  | Seconds |  |  |  |  |  |
| 14 | 4110 | 2384 | 1685 | 1192 | 973 | 688 | 487 | 397 | 344 |  | 308 |  |  |  |  |  |
| 12 | 6530 | 3787 | 2678 | 1894 | 1546 | 1093 | 773 | 631 | 547 |  | 489 |  |  |  |  |  |
| 10 | 10380 | 6020 | 4257 | 3010 | 2458 | 1738 | 1229 | 1003 | 869 |  | 777 |  |  |  |  |  |
| 8 | 16510 | 9575 | 6771 | 4788 | 3909 | 2764 | 1954 | 1596 | 1382 |  | 1236 |  |  |  |  |  |
| 6 | 26240 | 15218 | 10761 | 7609 | 6213 | 4393 | 3106 | 2536 | 2197 |  | 1965 |  |  |  |  |  |
| 4 | 41740 | 24207 | 17117 | 12104 | 9883 | 6988 | 4941 | 4035 | 3494 |  | 3125 |  |  |  |  |  |
| 3 | 52620 | 30517 | 21579 | 15259 | 12459 | 8810 | 6229 | 5086 | 4405 |  | 3940 |  |  |  |  |  |
| 2 | 66360 | 38486 | 27213 | 19243 | 15712 | 11110 | 7856 | 6414 | 5555 |  | 4968 |  |  |  |  |  |
| 1 | 83690 | 48536 | 34320 | 24268 | 19815 | 14011 | 9907 | 8089 | 7006 |  | 6266 |  |  |  |  |  |
| 1/0 | 105600 | 61243 | 43305 | 30621 | 25002 | 17679 | 12501 | 10207 | 8840 |  | 7906 |  |  |  |  |  |
| 2/0 | 133100 | 77192 | 54583 | 38596 | 31513 | 22283 | 15757 | 12865 | 11142 |  | 9965 |  |  |  |  |  |
| 3/0 | 167800 | 97316 | 68813 | 48658 | 39729 | 28093 | 19865 | 16219 | 14046 |  | 12563 |  |  |  |  |  |
| 4/0 | 211600 | 122718 | 86775 | 61359 | 50099 | 35426 | 25050 | 20453 | 17713 |  | 15843 |  |  |  |  |  |
| 250 | 250000 | 144988 | 102522 | 72494 | 59191 | 41854 | 29596 | 24165 | 20927 |  | 18718 |  |  |  |  |  |
| 300 | 300000 | 173986 | 123026 | 86993 | 71029 | 50225 | 35515 | 28998 | 25113 |  | 22461 |  |  |  |  |  |
| 350 | 350000 | 202983 | 143531 | 101492 | 82868 | 58596 | 41434 | 33831 | 29298 |  | 26205 |  |  |  |  |  |
| 400 | 400000 | 231981 | 164035 | 115990 | 94706 | 66967 | 47353 | 38663 | 33484 |  | 29949 |  |  |  |  |  |
| 500 | 500000 | 289976 | 205044 | 144988 | 118382 | 83709 | 59191 | 48329 | 41854 |  | 37436 |  |  |  |  |  |
| * When comparing these values for 1/2 cycle with the available RMS symmetrical fault current, multiply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| the available RMS symmetrical by 1.3 to account for asymmetry during the first half cycle. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

The next step to analyzing protection of conductors against short circuits depends upon the overcurrent device selected and available fault current.  The overcurrent protective device can either be a current limiting fuse or circuit breaker (current liming or non-current limiting).

Current Limiting Devices:

A device, which opens in one-half cycle or less, may or may not be classified as "current-limiting".  The device can be labeled current limiting only if it meets the requirements of UL/CSA (489/22.2 No. 5 for molded case circuit breakers or UL/CSA 248 for fuses).

The requirement for molded case circuit breakers is that the device must limit the asymmetrical fault current to a value below the equivalent symmetrical fault current.  If the circuit breaker is not current-limiting, but clears within approximately one-half cycle, the available symmetrical fault current must be multiplied by a factor of 1.3 to account for asymmetry.  Even if the molded case circuit breaker is current-limiting, the degree of current limitation is typically less than a rejection type fusible device.

The requirements for current-limiting fuses are based on the fuse type (Class) and upon the maximum I2t let-through as shown in Table 3.  If the device meets the performance criteria, it meets the standard for that class of fuse and can be listed/certified per UL/CSA.

The values shown in the table to the right can be used to compare the maximum I2t let-through for the fuse to the I2t rating of the conductor.  As long as the I2t let-through of the fuse is less than the I2t rating of the conductor, the conductor is protected under short-circuit conditions.

Table 3:

| Max Let-Through (Ampere2 Seconds) per UL 248 - Table A |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Fuse |  | I2t Max Let-through Value |  |  |  |  |  |
| Class |  | 50 | 100 | 200 |  |  |  |
|  |  | kA | kA | kA |  |  |  |
| Class J |  |  |  |  |  |  |  |
| 30 |  | 7,000 | 7,000 | 7,000 |  |  |  |
| 60 |  | 30,000 | 30,000 | 30,000 |  |  |  |
| 100 |  | 60,000 | 80,000 | 80,000 |  |  |  |
| 200 |  | 200,000 | 300,000 | 300,000 |  |  |  |
| 400 |  | 1,000,000 | 1,100,100 | 1,100,100 |  |  |  |
| 600 |  | 2,500,000 | 2,500,000 | 2,500,000 |  |  |  |
| Class RK1 |  |  |  |  |  |  |  |
| 30 |  | 10,000 | 10,000 | 11,000 |  |  |  |
| 60 |  | 40,000 | 40,000 | 50,000 |  |  |  |
| 100 |  | 100,000 | 100,000 | 100,000 |  |  |  |
| 200 |  | 400,000 | 400,000 | 400,000 |  |  |  |
| 400 |  | 1,200,000 | 1,200,000 | 1,600,000 |  |  |  |
| 600 |  | 3,000,000 | 3,000,000 | 4,000,000 |  |  |  |
| Class RK5 |  |  |  |  |  |  |  |
| 30 |  | 50,000 | 50,000 | 50,000 |  |  |  |
| 60 |  | 200,000 | 200,000 | 200,000 |  |  |  |
| 100 |  | 500,000 | 500,000 | 500,000 |  |  |  |
| 200 |  | 1,600,000 | 1,600,000 | 2,000,000 |  |  |  |
| 400 |  | 5,200,000 | 5,000,000 | 6,000,000 |  |  |  |
| 600 |  | 10,000,000 | 10,000,000 | 12,000,000 |  |  |  |
| Class T |  |  |  |  |  |  |  |
| 30 300V |  | 3,500 | 3,500 | 3,500 |  |  |  |
| 600V |  | 7,000 | 7,000 | 7,000 |  |  |  |
| 60 300V |  | 15,000 | 15,000 | 15,000 |  |  |  |
| 600V |  | 30,000 | 30,000 | 30,000 |  |  |  |
| 100 300V |  | 40,000 | 40,000 | 40,000 |  |  |  |
| 600V |  | 60,000 | 80,000 | 80,000 |  |  |  |
| 200 300V |  | 150,000 | 150,000 | 150,000 |  |  |  |
| 600V |  | 200,000 | 300,000 | 300,000 |  |  |  |
| 400 300V |  | 550,000 | 550,000 | 550,000 |  |  |  |
| 600V |  | 1,000,000 | 1,100,000 | 1,100,000 |  |  |  |
| 600 300V |  | 1,000,000 | 1,000,000 | 1,000,000 |  |  |  |
| 600V |  | 2,500,000 | 2,500,000 | 2,500,000 |  |  |  |

An example examining both the phase and grounding conductor is given on the following page.

Short-Circuit Protection of Wire and Cable:

Fusible Systems

The circuit shown originates at a distribution panel where 40,000 amperes RMS symmetrical are available. The # 10 THW copper conductor is protected by a Bussmann LOW-PEAK® fuse sized per NEC 240-3 (30A maximum for # 10 conductor).

Table 1, shows the I2t withstand rating of # 10 THW copper to be 301,994 000 ampere2 seconds per the ICEA Insulation damage level.  Since the Bussmann LOW-PEAK® is a Class RK1 current limiting fuse, the maximum I2t let-through per UL/CSA 248 can be found per the table on the previous page.  The maximum I2t let-through for a Class RK1 fuse at a fault not greater than 50,000A is 10,000 ampere2 seconds.  Since the I2t let-through of the fuse, 10,000, is considerably less than the I2t withstand of the # 10 conductor, 301,994, the conductor is protected against short-circuits.  In addition, since the minimum grounding conductor per NEC 250-122 is also # 10, the grounding conductor is protected as well.

Table 4, on the next page, compares the maximum I2t let-through for the fuse with the withstand of the conductor.  If the I2t withstand of the conductor is greater than the I2t let-through of the fuse; the conductor will be protected.  The table shows the minimum size conductor able to be protected under short-circuit conditions by the fusible device.

Circuit Breaker Systems

In the previous example a 30A, Class RK1 fuse was protecting a # 10 conductor.  If the 30A fusible device were replaced with a 30A, molded case circuit breaker with a clearing of 1/2 cycle would the # 10 conductor be protected?

Since the I2t let-through of the circuit breaker is not known, Tables 2 must be used.  If the 30A circuit breaker is current limiting, at a 40,000A fault, with a clearing time of 1/2 cycle, per UL 489, the let-through current could be as high as 40,000A RMS and still be marked current limiting.  If the device was not current limiting, the let-through current could be as high as 40,000 X 1.3, or 52,000A.  The maximum short-circuit current rating of # 10 conductor is 6,020A for 1/2 cycle (per ICEA).  Since the let-through current of either the current limiting or non-current limiting circuit breaker could be much greater than the short-circuit current rating of the conductor, protection can not be assured for either the phase or equipment grounding conductor.

Table 5, on the next page, can be utilized to analyze conductor protection by current-limiting and non-current limiting circuit breakers.  Note in the tables, the size of the conductor has increased due to the limited degree of current-limitation or the increased opening time of the device (compared to a fusible system).  When using molded case circuit breakers, insulated case circuit breakers or low voltage power circuit breakers, conductors must be carefully analyzed for protection.  This is especially true for equipment grounding conductors since the NEC allows for reduced sizing of the equipment grounding conductor despite the fact that available ground fault currents can be equal to or perhaps greater than the available three phase short-circuit currents.

Table 4:

| Conductor Short-Circuit Protection (ICEA Values) |  |  |  |  |  |  |  |  | Conductor Short-Circuit Protection (ICEA Values) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Minimum Conductor Size, Based on UL 248 |  |  |  |  |  |  |  |  | Minimum Conductor Size, Based on UL 248 |  |  |  |  |  |  |  |
| Fuse |  | Short-Circuit Current (RMS Amperes) |  |  |  |  |  |  | Fuse |  | Short-Circuit Current (RMS Amperes) |  |  |  |  |  |
| Class |  | 50 |  | 100 |  |  | 200 |  | Class |  | 50 |  | 100 |  |  | 200 |
|  |  | kA |  | kA |  |  | kA |  |  |  | kA |  | kA |  |  | kA |
| Class RK1 |  |  |  |  |  |  |  |  | Class J |  |  |  |  |  |  |  |
| 30 |  | 14 |  | 14 |  |  | 14 |  | 30 |  | 14 |  | 14 |  |  | 14 |
| 60 |  | 14 |  | 12 |  |  | 12 |  | 60 |  | 14 |  | 14 |  |  | 14 |
| 100 |  | 12 |  | 12 |  |  | 12 |  | 100 |  | 14 |  | 14 |  |  | 14 |
| 200 |  | 8 |  | 8 |  |  | 8 |  | 200 |  | 12 |  | 10 |  |  | 10 |
| 400 |  | 6 |  | 6 |  |  | 6 |  | 400 |  | 8 |  | 8 |  |  | 8 |
| 600 |  | 4 |  | 4 |  |  | 4 |  | 600 |  | 6 |  | 6 |  |  | 6 |
| Class RK5 |  |  |  |  |  |  |  |  | Class T |  |  |  |  |  |  |  |
| 30 |  | 12 |  | 12 |  |  | 12 |  | 30 300V |  | 14 |  | 14 |  |  | 14 |
| 60 |  | 10 |  | 10 |  |  | 10 |  | 600V |  | 14 |  | 14 |  |  | 14 |
| 100 |  | 8 |  | 8 |  |  | 8 |  | 60 300V |  | 14 |  | 14 |  |  | 14 |
| 200 |  | 6 |  | 6 |  |  | 4 |  | 600V |  | 14 |  | 14 |  |  | 14 |
| 400 |  | 3 |  | 3 |  |  | 3 |  | 100 300V |  | 14 |  | 14 |  |  | 14 |
| 600 |  | 2 |  | 2 |  |  | 2 |  | 600V |  | 14 |  | 14 |  |  | 14 |
|  |  |  |  |  |  |  |  |  | 200 300V |  | 12 |  | 12 |  |  | 12 |
|  |  |  |  |  |  |  |  |  | 600V |  | 12 |  | 10 |  |  | 10 |
|  |  |  |  |  |  |  |  |  | 400 300V |  | 10 |  | 10 |  |  | 10 |
|  |  |  |  |  |  |  |  |  | 600V |  | 8 |  | 8 |  |  | 8 |
|  |  |  |  |  |  |  |  |  | 600 300V |  | 8 |  | 8 |  |  | 8 |
|  |  |  |  |  |  |  |  |  | 600V |  | 6 |  | 6 |  |  | 6 |

Table 5:

| Circuit | Short-circuit Current (RMS Amperes) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Breaker's |  |  |  |  |  |  |  |  |  |
| (Clearing | 10 |  | 25 |  | 50 |  | 100 |  | 200 |
| or STD***) | kA |  | kA |  | kA |  | kA |  | kA |
| Setting |  |  |  |  |  |  |  |  |  |
| 1/2 cycle C.L.* | #6 |  | #3 |  | 1/0 |  | 4/0 |  | 350 |
| 1/2 cycle N.C.L.** | #6 |  | #2 |  | 2/0 |  | 250 |  | 500 |
| 1 Cycle | #6 |  | #2 |  | 2/0 |  | 250 |  | 500 |
| 3 Cycle | #3 |  | 1/0 |  | 4/0 |  | 500 |  | 900 |
| 6 Cycle | #2 |  | 3/0 |  | 300 |  | 600 |  | - |
| 12 Cycle | 1/0 |  | 4/0 |  | 500 |  | 900 |  | - |
| 18 Cycle | 1/0 |  | 300 |  | 600 |  | - |  | - |
| 24 Cycle | 2/0 |  | 300 |  | 600 |  | - |  | - |
| 30 Cycle | 3/0 |  | 350 |  | 700 |  | - |  | - |
| * C.L. = Current Limiting Circuit Breaker. Values are based upon UL 489/CSA 22.2 No. 5 |  |  |  |  |  |  |  |  |  |
| requirements to limit short-circuit currents to the symmetrical values. |  |  |  |  |  |  |  |  |  |
| ** N.C.L. = Non-Current Limiting Circuit Breaker *** STD = Short Time Delay |  |  |  |  |  |  |  |  |  |

The above material supplied by: Daniel R. Neeser, Manager, Technical Sales Cooper Bussmann

E-mail:  dneeser@buss.com, Website:  http://www.bussmann.com

Response No.1.

As I suspected, this article from Busmann is an attempt to "scare" people from using circuit breakers.  (Bussmann has numerous articles and videos that are produced using SELECTIVE DATA with the sole intention of discrediting the use of breakers.)  The fact is, that no matter how many theoretical calculations are performed, Power Circuit Breakers and Molded-Case Circuit breakers are lab-tested to UL standards WITH THE POWER CONDUCTORS AND LUGS attached to the circuit.  You can refer to the following standards:
UL1558 (standard for metal enclosed circuit breaker switchgear)
UL1066 (standard for power circuit breakers)
UL891 (standard for dead-front switchboards)
UL489 (standard for molded-case circuit breakers)

The reason some circuit breakers are intentionally designed with a short-time rating (typically large power breakers, above 800A), is to allow the downstream (usually current-limiting) feeders to clear the fault, so the main breaker stays closed to power the rest of the facility (Power System Coordination).  This is very critical in situations where losing power will cause loss of life, or where a critical process will be shut down unexpectedly (petro-chemical, steel mills, datacenters, etc.)  

This article also seems to overlook the fact that the wire itself tends to limit the fault current, due to conductor impedance.  Refering to the "theoretical" example illustrated in the article, if a fault occurs 10 feet away from a source that can deliver 40kA using #10 wire, the cable alone will limit the fault to about 10kA.  The author seems to think that 40kA gets passed through the conductor with zero impedance.  (For that matter, if the fault occurs in the wire, the wire will need to be replaced anyway...)

Other factors to consider: Line-connected fuses DO NOT offer ground-fault protection.

This was not made clear in the "Fusible Systems" example.  In the unlikely event that it is a "bolted" ground fault, and the prospective short-circuit current matches that of the primary circuit, only then will the fuse blow.  This, incidentally, will blow only one fuse in a 3-phase circuit, allowing the system to "single-phase", causing damage to downstream loads, such as motors.  In the practical application, bolted faults are the exception, not the norm (although the system MUST be designed to account for this situation).  Arcing faults in motors are the more common fault condition, which are normally low-magnitude.  More sensitive ground-fault equipment is required for this condition.  Circuit breakers offer this protection, along with the ability to open all 3 phases on a single line-ground fault. 

Where does Bussmann get the data for Table 5. Is this from UL, the NEC, IEEE, ICEA?  It appears this data is fabricated using zero lead-length conductors, with zero cable impedance.

Until real-world data is used, I recommend that you remove this newsletter from your outstanding web-site.  I very much enjoy the letters and examples that you supply to the industry.

If you have any additional questions, please feel free to contact me!!

Wayne Celeste
Cutler-Hammer District Application Engineer - Edison, NJ
celesw@ch.etn.com

Mike Holt’s Comment:

Nothing every changes, circuit breaker and fuse guys are always battling it out and this is good for the industry, it keeps every body on their toes.